A. Steps for a Drawing Review

The following is a basic listing of steps related to project drawing reviews. Included in this section is the current 	version of the Drawing Review Checklist dated 6/15/15.

- Issue notification of drawing review

- Request that consultants complete Drawing Review Checklist for use at the Drawing Review

- Review/Forward blank copy if necessary

- Review drawings

- Conduct drawing review

- Receive preliminary wattage calculations from A/E

- Complete Space Utilization Update Form and deliver it to the Space Planner who will review it for accuracy

B.	Drawing Review Checklist

Rev. 5/19/16

DRAWING REVIEW CHECKLIST

SITE

PROJECT:

CONSULTANT:

PROJECT MANAGER:

DATE:

|  |  | Yes | No | N/A | F/U | Remarks |
| --- | --- | --- | --- | --- | --- | --- |
| 1. | Has A/E reviewed final drawings of parking lot layout, truck dock, etc.? (Verify Quantity) | ( | ( | ( | ( | ________________________ |
| 2. | Do the accessible parking spaces comply with ADA? | ( | ( | ( | ( | ________________________ |
| 3. | Are accessible parking spaces located directly across from handicap ramps in close proximity to building entrances? | ( | ( | ( | ( | ________________________ |
| 4. | Do drawings indicate the required parking lot and ADA signage (Stop signs, No Parking, Fire Lane, etc.)? | ( | ( | ( | ( | ________________________ |
| 5. | Does new site lighting comply with code in terms of location of light standards and minimum illumination? | ( | ( | ( | ( | ________________________ |
| 6. | Are sidewalks free and clear of light poles, sign posts, etc.? | ( | ( | ( | ( | ________________________ |
| 7. | Have the Public Realm Lighting Design Standards been incorporated? |  |  |  |  |  |
| 8. | Have all utilities been shown, whether affected or not? | ( | ( | ( | ( | ________________________ |
| 9. | Has the responsibility for any and all utility work been clearly indicated? – Interferences? | ( | ( | ( | ( | ________________________ |
| 10. | Have any and all abandoned utility lines remaining in our building pad been specified to be removed or grouted? | ( | ( | ( | ( | ________________________ |
| 11. | Have legal documents been prepared for any existing easements to be abandoned? | ( | ( | ( | ( | ________________________ |
| 12. | Have legal documents been prepared for any new easements? Identify setbacks | ( | ( | ( | ( | ________________________ |
| 13. | Has pressure testing of utility lines been provided for, if required? | ( | ( | ( | ( | ________________________ |
| 14. | Have additional isolation valves in water/steam loop been provided to facilitate relocation of line? | ( | ( | ( | ( | ________________________ |
| 15. | Do drawings address utility switch over during non-operating hours? | ( | ( | ( | ( | ________________________ |
| 16. | Has the general extent and type of earthwork been indicated on the drawings in accordance with the Soils Report? | ( | ( | ( | ( | ________________________ |
|  | -Identify any future expansion |  |  |  |  |  |
| 17. | Has backfill placement been specified to be by the general contractor? | ( | ( | ( | ( | ________________________ |
|  |  | Yes | No | N/A | F/U | Remarks |
| 18. | Has the source of backfill material and disposal of spoils been addressed? | ( | ( | ( | ( | ________________________ |
| 19. | Is backfill material to be provided by others? | ( | ( | ( | ( | ________________________ |
| 20. | Does new pavement design comply with a “Design Period” of 20 years? (Permits) (20 years?) | ( | ( | ( | ( | ________________________ |
| 21. | Does new pavement design match existing? (Finish?) | ( | ( | ( | ( | ________________________ |
| 22. | Has existing paving that is to be left in place under fill areas been specified to be pulverized? | ( | ( | ( | ( | ________________________ |
| 23. | Has a Geo-Textile Fabric been specified under paved areas if required by Soils Report? | ( | ( | ( | ( | ________________________ |
| 24. | If existing paved areas to be resurfaced…. | ( | ( | ( | ( | ________________________ |
|  | - Is it a true overlay where required? | ( | ( | ( | ( | ________________________ |
|  | - Is it re-sealing only where required? | ( | ( | ( | ( | ________________________ |
| 25. | Is there a minimum 1’-0” elevation drop from finish floor elevation to top of perimeter sidewalk curb or adequate slope to maintain positive drainage away from building? | ( | ( | ( | ( | ________________________ |
| 26. | Has any transite (ACM) pipe been specified to be removed? | ( | ( | ( | ( | ________________________ |
| 27. | Do documents provide for pedestrian access over open trenches? (Truck Traffic?) | ( | ( | ( | ( | ________________________ |
| 28. | Has a site phasing plan been included? | ( | ( | ( | ( | ________________________ |
| 29. | Has the staging area been located? | ( | ( | ( | ( | ________________________ |
|  | - Is it 15,000 SF min.? | ( | ( | ( | ( | ________________________ |
|  | - Has a fence been provided? | ( | ( | ( | ( | ________________________ |
| 30. | Have permanent utility dates been specified? | ( | ( | ( | ( | ________________________ |
| 31. | Is contractor signage in place? | ( | ( | ( | ( | ________________________ |
| 32. | Are site drainage, retention & drainage inlets noted? | ( | ( | ( | ( | ________________________ |
| 33. | Has a contract limit been set? | ( | ( | ( | ( | ________________________ |
| 34. | Has construction access been identified? | ( | ( | ( | ( | ________________________ |
| 35. | Have requirements for fire hydrants been set? | ( | ( | ( | ( | ________________________ |
| 36. | Removal & reinstallation of parking and/or informational signage. Provide temporary signage? | ( | ( | ( | ( | ________________________ |
| 37. | Have alternate parking locations been discussed with Owner? | ( | ( | ( | ( | ________________________ |
| 38. | Has site lighting type & color been coordinated with Owner? | ( | ( | ( | ( | ________________________ |
| 39. | Has soil sampling been addressed for contamination? | ( | ( | ( | ( | ________________________ |
| 40. | If parking is part of the design, has security card swipes & gates been discussed with Owner? | ( | ( | ( | ( | ________________________ |
| 41. | Has routing of new utility line been discussed with Owner? | ( | ( | ( | ( | ________________________ |
| 42. | If a generator unit is installed on site, is the exhaust discharge close to any mechanical intakes? | ( | ( | ( | ( | ________________________ |
| 43. | Have drains been provided in utility man-holes? | ( | ( | ( | ( | ________________________ |

DRAWING REVIEW CHECKLIST

DEMOLITION

PROJECT:

CONSULTANT:

PROJECT MANAGER:

DATE:

|  |  | Yes | No | N/A | F/U | Remarks |
| --- | --- | --- | --- | --- | --- | --- |
| 1. | Have demolition drawings been coordinated with the Scope of Work/Final A/E documents? | ( | ( | ( | ( | ________________________ |
| 2. | Has WUSM environmental language (what is it?) been included in the documents per WUSM D&C Standards & Procedures? | ( | ( | ( | ( | ________________________ |
| 3. | Have disposal of fluorescent light tubes and ballasts been specified per WUSM D&C / EH&S Standards & Procedures? w/ disposal receipts called out – lamps/ballasts/f.a. | ( | ( | ( | ( | ________________________ |
| 4. | Is air being supplied to adjacent area at all times without dust being drawn into the system? (Filtration of air (Hepa filter) | ( | ( | ( | ( | ________________________ |
| 5. | Have HVAC filter changes been specified during demolition (min once per phase)? Use of construction HEPA filter | ( | ( | ( | ( | ________________________ |
| 6. | Has temporary lighting been provided where existing lighting is to be removed? | ( | ( | ( | ( | ________________________ |
| 7. | Have any reused or relocated items been clearly indicated? | ( | ( | ( | ( | ________________________ |
| 8. | Is the GC responsible for lab case work demolition? | ( | ( | ( | ( | ________________________ |
| 9. | Is the GC responsible for loose equipment relocation? (misc. equipment schedule) | ( | ( | ( | ( | ________________________ |
| 10. | Has existing concrete slab been specified to be prepared to receive new finishes? (Shotblast, chemicals, etc. to remove down to bare concrete) | ( | ( | ( | ( | ________________________ |
| 11. | Are there any special conditions (shoring, underpinning, etc.)? | ( | ( | ( | ( | ________________________ |
| 12. | Was an evaluation for Infection Control Procedures/Protocol performed? | ( | ( | ( | ( | ________________________ |
| 13. | Has additional cooling or heating that will be needed during any utility outage been addressed? | ( | ( | ( | ( | ________________________ |
| 14. | GC is responsible for the extra heating and cooling. | ( | ( | ( | ( | ________________________ |
| 15. | Has the proper sealing of holes in the exterior envelope of the building been addressed because of removal of piping, conduits, etc.? | ( | ( | ( | ( | ________________________ |
|  |  | Yes | No | N/A | F/U | Remarks |
| 16. | Has the removal of equipment supports on roofs and mechanical rooms because of the demolition of equipment been addressed? | ( | ( | ( | ( | ________________________ |
| 17. | Has temporary dedicated power been provided for demolition equipment? Spec item. | ( | ( | ( | ( | ________________________ |
| 18. | Have utility outages been coordinated with Owner for the removal of utilities in affected areas? | ( | ( | ( | ( | ________________________ |
| 19. | Smoke detectors need to be bagged in the demolition areas to prevent false fire alarm activation. | ( | ( | ( | ( | ________________________ |
| 20. | Telephone and data removal needs to be coordinated with the appropriate entities. | ( | ( | ( | ( | ________________________ |
| 21. | Fire alarm and building automation removal needs to be coordinated with the computer room. | ( | ( | ( | ( | ________________________ |

DRAWING REVIEW CHECKLIST

STRUCTURAL STEEL

PROJECT:

CONSULTANT:

PROJECT MANAGER:

DATE:

|  |  | Yes | No | N/A | F/U | Remarks |
| --- | --- | --- | --- | --- | --- | --- |
| 1. | Is steel exposed to weather specified to be galvanized? | ( | ( | ( | ( | ________________________ |
| 2. | Has prime painting of steel been included where required? | ( | ( | ( | ( | ________________________ |
| 3. | Are field painting and touch-up of structural steel included? | ( | ( | ( | ( | ________________________ |
| 4. | Is steel required to be fire-proofed? | ( | ( | ( | ( | ________________________ |
| 5. | Will metal deck accept spray-on fire proofing, if required | ( | ( | ( | ( | ________________________ |
| 6. | Has field painting and touch-up of metal roof deck included? | ( | ( | ( | ( | ________________________ |
| 7. | Does roof deck fluting have sufficient spacing to adequately support roof insulation? | ( | ( | ( | ( | ________________________ |
| 8. | Has the Structural Engineer investigated the seismic bracing of equipment? | ( | ( | ( | ( | ________________________ |
| 9. | Has the Structural Engineer investigated the requirements of vibration control thru the structure? | ( | ( | ( | ( | ________________________ |
| 10. | Has X-bracing been coordinated with egress locations? | ( | ( | ( | ( | ________________________ |
| 11. | Have all floor and roof openings for HVAC work been provided? | ( | ( | ( | ( | ________________________ |
| 12. | Has cutting of deck openings been specified? | ( | ( | ( | ( | ________________________ |
| 13. | Have steel drawings been coordinated with the owner’s Vertical Transportation vendor? | ( | ( | ( | ( | ________________________ |
| 14. | Have steel drawings been coordinated with the owner’s Cooling Tower vendor? | ( | ( | ( | ( | ________________________ |
| 15. | Has structural system been designed to provide for future expansion rights horizontally and/or vertically? | ( | ( | ( | ( | ________________________ |
| 16. | Has structural system been designed to accommodate fully loaded sprinkler and plumbing systems? | ( | ( | ( | ( | ________________________ |
| 17. | Have parapet and screen walls been properly braced? | ( | ( | ( | ( | ________________________ |
| 18. | Are shop drawings required to have an engineer’s seal? | ( | ( | ( | ( | ________________________ |
| 19. | Has a certified survey for building plumbness been specified? | ( | ( | ( | ( | ________________________ |
| 20. | Have miscellaneous metal and loose lintels been included? | ( | ( | ( | ( | ________________________ |
|  |  | Yes | No | N/A | F/U | Remarks |
| 21. | Has the design of CMU walls been verified with the Structural Engineer? | ( | ( | ( | ( | ________________________ |
| 22. | Has demolition and/or modification of existing structural steel been clearly indicated on the structural drawings? (expansion/remodel) | ( | ( | ( | ( | ________________________ |
| 23. | Have the shear walls been verified with the Structural Engineer? | ( | ( | ( | ( | ________________________ |
| 24. | Is steel contractor responsible for confirmation of all existing elevations and details at tie-in to existing buildings (expansions)? | ( | ( | ( | ( | ________________________ |
| 25. | Has the geo-technical consultant of record reviewed the drawings for conformance with soils report? | ( | ( | ( | ( | ________________________ |
| 26. | Has the engineer verified all miscellaneous equipment & storage units’ weights? | ( | ( | ( | ( | ________________________ |
| 27. | Have davits with look-out poles been provided? Has the structural engineer provided the load capacity of such system? | ( | ( | ( | ( | ________________________ |
| 28. | Has the added load, due to the use of light weight concrete deck, been incorporated into the roof design? | ( | ( | ( | ( | ________________________ |

DRAWING REVIEW CHECKLIST

BUILDING & CORE SHELL

PROJECT:

CONSULTANT:

PROJECT MANAGER:

DATE:

|  |  | Yes | No | N/A | F/U | Remarks |
| --- | --- | --- | --- | --- | --- | --- |
| 1. | Has Facilities Engineering provided building core & shell review comments? | ( | ( | ( | ( | ________________________ |
| 2. | Has the roof type been verified & has roof warranty research been performed? | ( | ( | ( | ( | ________________________ |
| 3. | Is the GC responsible for restoring the staging area upon removal? | ( | ( | ( | ( | ________________________ |
| 4. | Has a fence been specified around entire construction site? | ( | ( | ( | ( | ________________________ |
| 5. | Have landscaping beds been provided with adequate drainage away from the building? | ( | ( | ( | ( | ________________________ |
| 6. | Has topsoil been specified for planting areas? | ( | ( | ( | ( | ________________________ |
| 7. | Have landscaping beds been provided with an irrigation system? | ( | ( | ( | ( | ________________________ |
| 8. | Have sleeves been provided under concrete walks for irrigation line? | ( | ( | ( | ( | ________________________ |
| 9. | Will the irrigation system stop operation during rain? | ( | ( | ( | ( | ________________________ |
| 10. | Will the exterior wall section at planting beds prevent water infiltration into the building? What about the rest of the exterior wall section? | ( | ( | ( | ( | ________________________ |
| 11. | Have foundation bearing elevations been provided on foundation drawings? (Floor loads, Davit Loads) | ( | ( | ( | ( | ________________________ |
| 12. | Has a perimeter foundation drain been provided? | ( | ( | ( | ( | ________________________ |
| 13. | Have definitive bidding quantities and parameters for deep foundation system been specified? | ( | ( | ( | ( | ________________________ |
| 14. | Has the exterior wall system (brick veneer, EIFS, etc.) been detailed to be above grade. | ( | ( | ( | ( | ________________________ |
| 15. | Has the curtain wall system been fully designed by the A/E? | ( | ( | ( | ( | ________________________ |
| 16. | Have all reveals, control joints in the exterior wall, etc. been designed & detailed in strict accordance with the approved curtain wall design? | ( | ( | ( | ( | ________________________ |
| 17. | Has “Dens-Glas” only been specified for the building sheathing? Alternate? | ( | ( | ( | ( | ________________________ |
| 18. | Has Tyvek, wrap or spray foam only been specified for brick veneer wall systems? | ( | ( | ( | ( | ________________________ |
|  |  | Yes | No | N/A | F/U | Remarks |
| 19. | Have galvanized relief angles been provided in masonry walls? | ( | ( | ( | ( | ________________________ |
| 20. | Have stainless steel fasteners been specified? | ( | ( | ( | ( | ________________________ |
| 21. | Has the back of parapets been detailed with metal panels? | ( | ( | ( | ( | ________________________ |
| 22. | Has the roofing system design been coordinated with the height of the parapet? | ( | ( | ( | ( | ________________________ |
| 23. | Has building signage been specified? | ( | ( | ( | ( | ________________________ |
| 24. | Has the dock seal been detailed to be sealed tight to the wall? | ( | ( | ( | ( | ________________________ |
| 25. | Has coping been detailed? | ( | ( | ( | ( | ________________________ |
| 26. | Have concrete admixtures been specified as unacceptable in the concrete mix design without owner’s approval? | ( | ( | ( | ( | ________________________ |
| 27. | Verify with Owner the use of flyash in the concrete mix design. | ( | ( | ( | ( | ________________________ |
| 28. | Have roof details been provided in accordance with WUSM Standards? | ( | ( | ( | ( | ________________________ |
| 29. | Has the current WUSM roof warranty been included? (10 year roof) | ( | ( | ( | ( | ________________________ |
| 30. | Has roof hatch & access system been specified? | ( | ( | ( | ( | ________________________ |
| 31. | Has a hand-crank jib hoist been provided at upper level penthouse? | ( | ( | ( | ( | ________________________ |
| 32. | Has a ship’s ladder been provided to roof? – Is there access to all roofs? Caged? | ( | ( | ( | ( | ________________________ |
| 33. | Have roof walkway pads been provided from roof hatches to penthouse and cooling tower only? | ( | ( | ( | ( | ________________________ |
| 34. | Have the specifications been coordinated with WUSM D&C’s Testing and Inspection program? | ( | ( | ( | ( | ________________________ |
| 35. | Have the toilet rooms been designed per current WUSM D&C standards? | ( | ( | ( | ( | ________________________ |
| 36. | Have the current toilet room finishes and colors been specified? | ( | ( | ( | ( | ________________________ |
| 37. | Have all walls of toilet rooms been drawn in elevation? | ( | ( | ( | ( | ________________________ |
| 38. | Has Denz Deck drywall been specified for wet wall? | ( | ( | ( | ( | ________________________ |
| 39. | Have all toilet room accessories been coordinated with WUSM FMD? | ( | ( | ( | ( | ________________________ |
| 40. | Are permanent building hardware cores to be furnished & installed by the GC? | ( | ( | ( | ( | ________________________ |
| 41. | Will the drawings be submitted for building permit after bids are received? | ( | ( | ( | ( | ________________________ |
| 42. | Are there glass cleaning & requirements in place? | ( | ( | ( | ( | ________________________ |
| 43. | Has Dow Corning 795 Silicone Sealant been specified for all glazing, metal to metal, & metal to glass joints? (When going from the above to masonry, must prime masonry first.) | ( | ( | ( | ( | ________________________ |
|  |  | Yes | No | N/A | F/U | Remarks |
| 44. | Has Dow Corning 790 Silicone Sealant been specified for all stone to stone, stone to brick, & brick to brick joints? (When going from the above to metal, must prime metal first.) | ( | ( | ( | ( | ________________________ |
| 45. | Are end dams provided at all relief angles? | ( | ( | ( | ( | ________________________ |
| 46. | Are relief angles called out to be continuous at the same elevations and not at multiple heights in a “stair step” fashion? | ( | ( | ( | ( | ________________________ |
| 47. | Are relief angles called out to be continuous and that the flashing covers the complete angle? | ( | ( | ( | ( | ________________________ |
| 48. | Has it been called out that the EIFS system must be completely finished on the bottom edge? | ( | ( | ( | ( | ________________________ |
| 49. | Have inserts been laid out for hangers for utilities and mechanical equipment on post-tensioned construction? | ( | ( | ( | ( | ________________________ |
| 50. | Have proper supports been called out for any piping or electrical that will be routed on the roof and do they comply with the roofing manufactures recommendation? | ( | ( | ( | ( | ________________________ |
| 51. | Has temporary construction power been provided to erect the shell & core? (Spec item) | ( | ( | ( | ( | ________________________ |
| 52. | Have spare sleeves to the outside of the building been installed in an accessible location for the installation of future systems? Have sleeves been sealed and capped? | ( | ( | ( | ( | ________________________ |
| 53. | Have access panels/doors been sized in mechanical/electrical and elevator machine rooms so that equipment can be easily removed and replaced? | ( | ( | ( | ( | ________________________ |
| 54. | Does the building receive and ground ring electrode? | ( | ( | ( | ( | ________________________ |
| 55. | Does the building receive a lightning protection system, and if so, is it tied to the ground ring electrode? | ( | ( | ( | ( | ________________________ |
| 56. | Are the electrical ground, telephone ground, data ground, structural steel, water piping and lightning protection all tied together? | ( | ( | ( | ( | ________________________ |
| 57. | Are the electrical, data/phone closets aligned on multi story buildings whenever possible? | ( | ( | ( | ( | ________________________ |
| 58. | Have mechanical risers (piping & ductwork) been installed away from electrical and communication closets? | ( | ( | ( | ( | ________________________ |
| 59. | Have sump pumps been installed in elevator pits and at the lowest building level? | ( | ( | ( | ( | ________________________ |
| 60. | Have 120/208V risers for receptacle loads and 277/480V risers been installed for lighting loads for new construction? | ( | ( | ( | ( | ________________________ |

DRAWING REVIEW CHECKLIST

BUILDING INTERIORS

PROJECT:

CONSULTANT:

PROJECT MANAGER:

DATE:

|  |  | Yes | No | N/A | F/U | Remarks |
| --- | --- | --- | --- | --- | --- | --- |
| 1. | Has the Special System meeting been held? (date?) | ( | ( | ( | ( | ________________________ |
| 2. | Has a Special Systems meeting report been published? | ( | ( | ( | ( | ________________________ |
| 3. | Have any and all items which will be exposed in the ceiling plenum been specified for use in a plenum? | ( | ( | ( | ( | ________________________ |
| 4. | Is there an ADA accessible path of travel from parking lot to inside of building? (Remodels) | ( | ( | ( | ( | ________________________ |
| 5. | Are all toilet rooms ADA accessible? (Remodels) | ( | ( | ( | ( | ________________________ |
| 6. | Has the door hardware been coordinated with any card reader access functions? | ( | ( | ( | ( | ________________________ |
| 7. | Is there adequate space at fire alarm panel location for firemen access? | ( | ( | ( | ( | ________________________ |
| 8. | Are permanent building hardware cores furnished & installed by the GC? | ( | ( | ( | ( | ________________________ |
| 9. | Are the floor patterns laid out? (VCT, CT, CR, etc.) | ( | ( | ( | ( | ________________________ |
| 10. | Are the locations of M, E, P, FP items in public areas (lobby, atrium area, etc.) approved? | ( | ( | ( | ( | ________________________ |
| 11. | Have the fire extinguisher cabinet’s locations been specified? | ( | ( | ( | ( | ________________________ |
| 12. | Are any “Areas of Refuge” needed, and clearly spelled out? | ( | ( | ( | ( | ________________________ |
| 13. | Have the electrical loads been checked so that panels installed under the shell & core are not overloaded? | ( | ( | ( | ( | ________________________ |
| 14. | No emergency battery lighting units to be used on buildings with an emergency generator. | ( | ( | ( | ( | ________________________ |
| 15. | Have all conduit, cable tray, piping ductwork, etc. that penetrate a fire rated wall been sealed with U.L. listed fire rated material or assembly? | ( | ( | ( | ( | ________________________ |
| 16. | Have all conduit, cable tray, ductwork, etc. that penetrate a standard rated wall been sealed? | ( | ( | ( | ( | ________________________ |
| 17. | Are there any single stall restrooms and have they been labeled with signage as for unisex use? | ( | ( | ( | ( | _______________________ |

DRAWING REVIEW CHECKLIST

DRYWALL/ACOUSTICAL

PROJECT:

CONSULTANT:

PROJECT MANAGER:

DATE:

|  |  | Yes | No | N/A | F/U | Remarks |
| --- | --- | --- | --- | --- | --- | --- |
| 1. | Is toilet room chase wall deep enough to allow for WC carriers? Toilets with auto flush valves specified without toilet seat covers? Has grab bar height been coordinated w/ flush valve height? | ( | ( | ( | ( | ________________________ |
| 2. | Has plywood been specified in all electrical / data room’s fire rated? | ( | ( | ( | ( | ________________________ |
| 3. | Have control joints been detailed in drywall ceilings and soffits? | ( | ( | ( | ( | ________________________ |
| 4. | Has water resistant Denz Deck drywall been provided at toilet rooms and janitor’s closet? | ( | ( | ( | ( | ________________________ |
| 5. | Has fire retardant wood and/or metal plate blocking been specified? | ( | ( | ( | ( | ________________________ |
| 6. | Has all concealed blocking been specified as fire-retardant? | ( | ( | ( | ( | ________________________ |
| 7. | Have all required fire-rated partitions been provided and detailed? (Provide tested assembly #’s) | ( | ( | ( | ( | ________________________ |
| 8. | Has all drywall been standardized to be 5/8” thick? | ( | ( | ( | ( | ________________________ |
| 9. | Has the existing drywall thickness been verified? (Remodels) | ( | ( | ( | ( | ________________________ |
| 10. | Has it been clearly specified that the contractor is responsible for all hanger wires, wall angles, clips etc. required to install the ACT ceiling? And all seismic bracing? | ( | ( | ( | ( | ________________________ |
| 11. | Has it been clearly specified who is to furnish and install the hanger wires for the 2x2 light fixtures? – Seismic support – verify details? | ( | ( | ( | ( | ________________________ |
| 12. | Have all partitions requiring sound batts been identified? | ( | ( | ( | ( | ________________________ |
| 13. | Have the following finishes for conformance to standards been reviewed? | ( | ( | ( | ( | ________________________ |
|  | Floor types – VCT, seamless, epoxy, carpet (roll, tile), other – wood by exception | ( | ( | ( | ( | ________________________ |
|  | Wall finishes – paint types – low VOC | ( | ( | ( | ( | ________________________ |
|  | Wallcovering – by exception only | ( | ( | ( | ( | ________________________ |
|  | Glass – thickness – film type – no etching | ( | ( | ( | ( | ________________________ |
|  | Wall base – type – height | ( | ( | ( | ( | ________________________ |
|  |  | Yes | No | N/A | F/U | Remarks |
|  | Marker boards | ( | ( | ( | ( | ________________________ |
|  | Bulletin boards | ( | ( | ( | ( | ________________________ |
|  | Coordination of light switch, thermostat, fire alarm devices – outlets, data | ( | ( | ( | ( | ________________________ |
|  | Clearances and service locations related to furniture and equipment | ( | ( | ( | ( | ________________________ |
|  | Wall protection in high-abuse areas | ( | ( | ( | ( | ________________________ |
|  | Interior signage | ( | ( | ( | ( | ________________________ |
| 14. | Have access panels been provided for equipment that will be covered by drywall? (i.e., values, regulators, VAVs) | ( | ( | ( | ( | ________________________ |
| 15. | Have light fixtures been coordinated with ceiling layout and type of ceiling? | ( | ( | ( | ( | ________________________ |
| 16. | Has the acoustical ceiling layout been coordinated between the light fixtures, mechanical grills, sprinkler heads, fire alarm and motion sensors? | ( | ( | ( | ( | ________________________ |

-

DRAWING REVIEW CHECKLIST

MECHANICAL

PROJECT:

CONSULTANT:

PROJECT MANAGER:

DATE:

|  |  | Yes | No | N/A | F/U | Remarks |
| --- | --- | --- | --- | --- | --- | --- |
| 1. | Has the Systems Commissioning program been incorporated into the documents in accordance with WUSM D&C Standards and Procedures? | ( | ( | ( | ( | ________________________ |
| 2. | Have temporary mechanical system controls been specified? | ( | ( | ( | ( | ________________________ |
| 3. | Have an adequate amount of filter changes been specified (one per phase minimum)? (Comply with LEED) | ( | ( | ( | ( | ________________________ |
| 4. | Has a minimum relative humidity been specified at the start of Drywall work? | ( | ( | ( | ( | ________________________ |
| 5. | Is ductwork and piping specified to be tight to structure/high as possible? | ( | ( | ( | ( | ________________________ |
| 6. | Are insulated supply ducts required? Is no internally lined ductwork specified? | ( | ( | ( | ( | ________________________ |
| 7. | Is seismic bracing required for duct work or piping? | ( | ( | ( | ( | ________________________ |
| 8. | Have fire dampers been provided at all rated walls? | ( | ( | ( | ( | ________________________ |
| 9. | Have outside air/air change requirements been provided for? | ( | ( | ( | ( | ________________________ |
| 10. | Has the mechanical system been designated to provide for any future expansion? | ( | ( | ( | ( | ________________________ |
| 11. | Has propylene glycol been specified? | ( | ( | ( | ( | ________________________ |
| 12. | Will all exterior piping be painted (gas, oil, water, etc.)? | ( | ( | ( | ( | ________________________ |
| 13. | Has refrigerant leak protection been provided in the mechanical room? | ( | ( | ( | ( | ________________________ |
| 14. | Has local thermostatic control been provided in the general offices? | ( | ( | ( | ( | ________________________ |
| 15. | Has access been provided for all fire, smoke and volume dampers? | ( | ( | ( | ( | ________________________ |
| 16. | Has a maximum flex duct length of 5’-0” been detailed and specified? | ( | ( | ( | ( | ________________________ |
| 17. | Have VFD’s been provided for all appropriate mechanical components? | ( | ( | ( | ( | ________________________ |
| 18. | Has perimeter heat been provided where required? | ( | ( | ( | ( | ________________________ |
| 19. | Has toilet room exhaust been adequately sized? | ( | ( | ( | ( | ________________________ |
|  |  | Yes | No | N/A | F/U | Remarks |
| 20. | Have exhaust fans been located a sufficient distance from outside air intakes? | ( | ( | ( | ( | ________________________ |
| 21. | Has the height of roof curbs and exhaust fans been coordinated with parapet heights? | ( | ( | ( | ( | ________________________ |
| 22. | Do specifications clearly indicate how HVAC system will be controlled prior to BAS system complete? | ( | ( | ( | ( | ________________________ |
| 23. | Does turning vane detail refer to SMACNA standards and/or specify cut off point for 2” and 4 ½” vanes? | ( | ( | ( | ( | ________________________ |
| 24. | Has new duct work installation been coordinated with existing steel heights (Remodels)? | ( | ( | ( | ( | ________________________ |
| 25. | Have supply diffusers been located away from smoke detectors? | ( | ( | ( | ( | ________________________ |
| 26. | Have clearances & access to all equipment & replacement parts been evaluated for ongoing maintenance? | ( | ( | ( | ( | ________________________ |
| 27. | Has access been provided to all valves? | ( | ( | ( | ( | ________________________ |
| 28. | Have louver locations & sizes been specified? | ( | ( | ( | ( | ________________________ |
| 29. | Are roof drain pipes insulated? | ( | ( | ( | ( | ________________________ |
| 30. | Are AHU condensate drains insulated? | ( | ( | ( | ( | ________________________ |
| 31. | Stairwell pressurization fans accessible for maintenance? | ( | ( | ( | ( | ________________________ |
| 32. | Is all building equipment serviceable without scaffolding? | ( | ( | ( | ( | ________________________ |
| 33. | Are all AHU bird screens accessible for periodic cleaning? | ( | ( | ( | ( | ________________________ |
| 34. | Has mechanical equipment been isolated to prevent noise & vibration transmission? | ( | ( | ( | ( | ________________________ |
| 35. | Are closing dampers provided for any louvers installed in mechanical spaces to prevent line freezes? | ( | ( | ( | ( | ________________________ |
| 36. | Mechanical coordination – Do we have a minimum of 5’ clearance for access to interstitial equipment space MEPFS? | ( | ( | ( | ( | ________________________ |
| 37. | Has the HVAC equipment serving offices/labs/etc. been properly located for maintenance purposes? | ( | ( | ( | ( | ________________________ |
| 38. | Has all outdoor hot & cold water piping, condensate return, drain, tower piping shall be heat traced, and have an extra trace installed but not wired? | ( | ( | ( | ( | ________________________ |
| 39. | Do all heat trace lines not connected to a main control panel have end of line pilot light, to verify their functionality? | ( | ( | ( | ( | ________________________ |
| 40. | Has the supply diffuser location been coordinated with motion sensor locations? | ( | ( | ( | ( | ________________________ |
| 41. | Vestibule/air control/air curtain – Is there air control / air curtain in the vestibule entrance? | ( | ( | ( | ( | ________________________ |
| 42. | On remodels with return air, is dust control in place? | ( | ( | ( | ( | ________________________ |

DRAWING REVIEW CHECKLIST

ELECTRICAL

PROJECT:

CONSULTANT:

PROJECT MANAGER:

DATE:

|  |  | Yes | No | N/A | F/U | Remarks |
| --- | --- | --- | --- | --- | --- | --- |
| 1. | Have the current electrical design criteria sheets been incorporated? | ( | ( | ( | ( | ________________________ |
| 2. | Have the requirement & specifications for emergency power been reviewed with the Owner? | ( | ( | ( | ( | ________________________ |
| 3. | Is voice/data cable specified to be furnished and installed by the electrical contractor? | ( | ( | ( | ( | ________________________ |
| 4. | Is voice/data cable specification per WUSM D&C Standards & Procedures? | ( | ( | ( | ( | ________________________ |
| 5. | Have occupancy sensors been provided per WUSM D&C Standards & Procedures? | ( | ( | ( | ( | ________________________ |
| 6. | Is a separate telephone required at the fire alarm panel? | ( | ( | ( | ( | ________________________ |
| 7. | Has an allowance of extra “Exit” lights been specified? | ( | ( | ( | ( | ________________________ |
| 8. | Is any seismic bracing required for light fixtures? | ( | ( | ( | ( | ________________________ |
| 9. | Is there any seismic bracing for all electrical pipe, equipment, lights, etc? | ( | ( | ( | ( | ________________________ |
| 10. | Have electrical rooms been designed to accommodate all panels, equipment, etc. w/ proper clearing and some room for expansion? | ( | ( | ( | ( | ________________________ |
| 11. | Are there any provisions for temporary HVAC controls? | ( | ( | ( | ( | ________________________ |
| 12. | Is conduit specified to be tight to structure/high as possible? | ( | ( | ( | ( | ________________________ |
| 13. | Have lighting plans been submitted to WUSM D&C? | ( | ( | ( | ( | ________________________ |
| 14. | Have electrical room numbers been provided? | ( | ( | ( | ( | ________________________ |
| 15. | Have the roof drains and plumbing lines been coordinated with the electrical drawings? | ( | ( | ( | ( | ________________________ |
| 16. | Is it clearly specified as to who furnishes and installs light fixture hanger wires (EC or DW)? | ( | ( | ( | ( | ________________________ |
| 17. | Will the BAS drawings be required to be sealed? | ( | ( | ( | ( | ________________________ |
| 18. | Have all the Special Systems requirements been incorporated into the documents? | ( | ( | ( | ( | ________________________ |
| 19. | Are electrical panel schedules complete? Specified to be neatly typed panel listings in each breaker panel, plus a copy of each legend in the final documents given to us? | ( | ( | ( | ( | ________________________ |
|  |  | Yes | No | N/A | F/U | Remarks |
| 20. | Have voltage and horsepower requirements been coordinated with the mechanical drawings? | ( | ( | ( | ( | ________________________ |
| 21. | Is it specified for the architect to approve all devices in public spaces (lobby, atrium area, etc.) | ( | ( | ( | ( | ________________________ |
| 22. | Do roof lighting requirements meet FAA (height of building)? | ( | ( | ( | ( | ________________________ |
| 23. | Has lighting protection been provided? | ( | ( | ( | ( | ________________________ |
| 24. | If emergency power is needed, has the equipment and outlet locations been identified? | ( | ( | ( | ( | ________________________ |
| 25. | Have grounding risers for tele/data & power been separated and all been tied together at main electrical ground bar? | ( | ( | ( | ( | ________________________ |
| 26. | Are elevator shafts and machine room’s air conditioned? | ( | ( | ( | ( | ________________________ |
| 27. | Is GFI in pit(s) and near elevator controller? | ( | ( | ( | ( | ________________________ |
| 28. | Is conduit installed from ATS to elevator controller for pre transfer signal from ATS to elevator controller? | ( | ( | ( | ( | ________________________ |
| 29. | No in slab conduit? | ( | ( | ( | ( | ________________________ |
| 30. | Have the light fixtures been reviewed by D&C & user? | ( | ( | ( | ( | ________________________ |
| 31. | Have lamp types been compared to light bulb stock list? Deviation by exception. | ( | ( | ( | ( | ________________________ |
| 32. | Have the size and design of voice/data closets been signed off and approved by TFC/Networking Services? | ( | ( | ( | ( | ________________________ |
| 33. | Are the new building voltages 5Kv primary, 480 volt secondary, with the lab/office voltages of 208/120? | ( | ( | ( | ( | ________________________ |
| 34. | Depending on the building usage, is the main substation double ended with automatic tie capabilities? | ( | ( | ( | ( | ________________________ |
| 35. | Do outdoor and building substations have arc fault mitigation? | ( | ( | ( | ( | ________________________ |
| 36. | Are all building electrical substations, transformers, distribution gear, MCC, disconnects and panels manufactured by Eaton or Square D? | ( | ( | ( | ( | ________________________ |
| 37. | Do new building substations have draw-out style main and tie breakers? | ( | ( | ( | ( | ________________________ |
| 38. | Is electrical metering by Square D/Power Logic? | ( | ( | ( | ( | ________________________ |
| 39. | Does all new electrical work have a coordination study by a third party? | ( | ( | ( | ( | ________________________ |
| 40. | Is all new (substantially sized) electrical work commissioned by a third party? | ( | ( | ( | ( | ________________________ |
| 41. | Does all new (substantial sized) electrical work have a set of each type of fuse used in such electrical gear and a wall hung fuse cabinet? | ( | ( | ( | ( | ________________________ |
| 42. | Do all 208/120 volt panels have 20 amp breakers as their minimum size? | ( | ( | ( | ( | ________________________ |
| 43. | Are all new electrical rooms with and without transformers air conditioned? | ( | ( | ( | ( | ________________________ |
|  |  | Yes | No | N/A | F/U | Remarks |
| 44. | For new construction projects, was the following color coded EMT (conduit) used? | ( | ( | ( | ( | ________________________ |
|  | Emergency ckts: Red | ( | ( | ( | ( | ________________________ |
|  | Security & special ckts: Purple | ( | ( | ( | ( | ________________________ |
|  | Low voltage ckts: Blue | ( | ( | ( | ( | ________________________ |
|  | Health Care ckts: Green | ( | ( | ( | ( | ________________________ |
| 45. | Are all receptacles and switches hospital grade? | ( | ( | ( | ( | ________________________ |
| 46. | Are all receptacles & switches 20 amp? | ( | ( | ( | ( | ________________________ |
| 47. | Are all lab wire ways aluminum Wiremold or Versa-Duct? | ( | ( | ( | ( | ________________________ |
| 48. | Do all pre-wired wire ways use wire nuts or wing nuts for all wire splices? No crimp connectors should be used. | ( | ( | ( | ( | ________________________ |
| 49 | If new/tall building, is it verified if there is a need for aircraft warning lights? | ( | ( | ( | ( | ________________________ |
| 50. | Have building standards been referred to for fixture style in offices, labs, hallways etc.? | ( | ( | ( | ( | ________________________ |
| 51. | Have fluorescent T8 lamps with 28 watt electronic ballast been used for all standard ceiling lighting? | ( | ( | ( | ( | ________________________ |
| 52. | Are lamps specified to meet our standard lamp rating at 4100 Kelvin? | ( | ( | ( | ( | ________________________ |
| 53. | Are all recessed can fixtures fluorescent? LED to be used in hard to access locations. | ( | ( | ( | ( | ________________________ |
| 54. | Does all hallway, restroom lighting have ultrasonic/infrared switching sensors? | ( | ( | ( | ( | ________________________ |
| 55. | Do all branch circuits have dedicated neutrals? | ( | ( | ( | ( | ________________________ |
| 56. | Has the type and size of cable tray been coordinated with WUSM? | ( | ( | ( | ( | ________________________ |
| 57. | Do all buildings have a minimum of two automatic transfer switches, a life safety ATS and an optional standby ATS? | ( | ( | ( | ( | ________________________ |
| 58. | Are motion sensors used in offices, labs and corridors? Are countdown timers used in mechanical and electrical rooms? | ( | ( | ( | ( | ________________________ |
| 59. | Does the main electrical substation(s) have Square-D power logic metering for logging data? | ( | ( | ( | ( | ________________________ |
| 60. | On new building construction. Has a Schneider Electric WAGES system been installed which meters the buildings chilled water, steam and electrical usage? System to be tied into the North building basement Struxtureware system and programmed. | ( | ( | ( | ( | ________________________ |
| 61. | On new building construction. Are the double ended Substation(s) Main & Tie breakers the rack-out type? | ( | ( | ( | ( | ________________________ |
| 62. | On new building construction. Has an ALERTUS system been installed that connects into the building fire alarm system for mass notification? | ( | ( | ( | ( | ________________________ |

DRAWING REVIEW CHECKLIST

PLUMBING

PROJECT:

CONSULTANT:

PROJECT MANAGER:

DATE:

|  |  | Yes | No | N/A | F/U | Remarks |
| --- | --- | --- | --- | --- | --- | --- |
| 1. | Has all piping been specified to be tight to structure/high as possible? | ( | ( | ( | ( | ________________________ |
| 2. | Is seismic bracing required for piping? | ( | ( | ( | ( | ________________________ |
| 3. | Has a floor drain been omitted at water treatment chemical storage area? | ( | ( | ( | ( | ________________________ |
| 4. | Has a splash block/concrete been provided at through-wall storm drain overflow outlet? | ( | ( | ( | ( | ________________________ |
| 5. | Is the elevator sump piped to sanitary system? | ( | ( | ( | ( | ________________________ |
| 6. | Has the roof drain piping been coordinated with the M, E, FP drawings? | ( | ( | ( | ( | ________________________ |
| 7. | Has exposed gas piping been specified to be painted/touched up? | ( | ( | ( | ( | ________________________ |
| 8. | Has a high water / loss of power alarm contact been provided at the elevator sump? | ( | ( | ( | ( | ________________________ |
| 9. | Has landscape irrigation system been coordinated with the plumbing drawings? | ( | ( | ( | ( | ________________________ |
| 10. | Are all lavatories and faucets ADA compliant/touchless? | ( | ( | ( | ( | ________________________ |
| 11. | Are horizontal runs of roof drains specified to be insulated? | ( | ( | ( | ( | ________________________ |
| 12. | Has piping been specified in accordance with soils report (corrosion resistance, etc.)? | ( | ( | ( | ( | ________________________ |
| 13. | Has location of clean outs at sink and toilets been coordinated w/ FE? | ( | ( | ( | ( | ________________________ |
| 14. | Is power shown for the locations of hand free faucets? | ( | ( | ( | ( | ________________________ |
| 15. | Are there any devices or equipment that can either use or produce extremely high water temperatures and are they connected to any drains that are made of plastic? | ( | ( | ( | ( | ________________________ |
| 16. | Has the building reduced pressure zone back-flow device been located in an area for ease of testing and maintenance and is no higher than 6’ above the floor? | ( | ( | ( | ( | ________________________ |
| 17. | Have drains and vents been installed in liquid pipes that have low spots? | ( | ( | ( | ( | ________________________ |

DRAWING REVIEW CHECKLIST

FIRE PROTECTION

PROJECT:

CONSULTANT:

PROJECT MANAGER:

DATE:

|  |  | Yes | No | N/A | F/U | Remarks |
| --- | --- | --- | --- | --- | --- | --- |
| 1. | Is piping specified to be installed as high as possible? | ( | ( | ( | ( | ________________________ |
| 2. | Is seismic bracing required for piping? | ( | ( | ( | ( | ________________________ |
| 3. | Have glass bulb or fusable link sprinklers been specified? | ( | ( | ( | ( | ________________________ |
| 4. | Has sprinkler head location tolerances within acoustical ceiling tiles been specified? | ( | ( | ( | ( | ________________________ |
| 5. | Has sprinkler head centerline alignment criteria been specified? | ( | ( | ( | ( | ________________________ |
| 6. | Have the FM contacts been specified? | ( | ( | ( | ( | ________________________ |
| 7. | Have the flow alarms and tamper switches been coordinated with the mechanical and electrical drawings and specifications? | ( | ( | ( | ( | ________________________ |
| 8. | Has water flow test data been incorporated onto the specifications? | ( | ( | ( | ( | ________________________ |
| 9. | Has a schedule 40 sprinkler piping been specified? | ( | ( | ( | ( | ________________________ |
| 10. | Is there an express drain installed for flow testing? | ( | ( | ( | ( | ________________________ |
| 11. | Has a 286 degree temperature rated sprinkler head been called out for in an autoclave area? | ( | ( | ( | ( | ________________________ |
| 12. | Are duct detectors monitoring smoke for Air Handlers connected to the building fire alarm system? | ( | ( | ( | ( | ________________________ |
| 13. | Is the building fire alarm system communicating with the Facilities Engineering Control Room in the North building? | ( | ( | ( | ( | ________________________ |
| 14. | Was the system designed around a Siemens or Notifier standard system? | ( | ( | ( | ( | ________________________ |
| 15. | Has fire pump been sized properly? If connected to a generator, provide with internal ATS. | ( | ( | ( | ( | ________________________ |
| 16. | Do the temperature control cabinets have dedicated electrical power? | ( | ( | ( | ( | ________________________ |
| 17. | Is all of the Animal Facility temperature control equipment on emergency power? | ( | ( | ( | ( | ________________________ |
| 18. | Is C&C Group installing a BACnet or LONworks Building Automation System? | ( | ( | ( | ( | ________________________ |
| 19. | Is Johnson Controls installing a BACnet or LONworks Building Automation System? | ( | ( | ( | ( | ________________________ |
|  |  | Yes | No | N/A | F/U | Remarks |
| 20. | Has an Ethernet drop installation been requested through the Central I.T. website for the Building Automation System? | ( | ( | ( | ( | ________________________ |
| 21. | Is the Building Automation System communicating with the Facilities Engineering Control Room in the North Building? | ( | ( | ( | ( | ________________________ |
| 22. | Are any of the existing Honeywell Building Automation Controls being replaced with C&C Group LONworks system in 4444 Forest Park building? | ( | ( | ( | ( | ________________________ |
| 23. | Are any of the existing C&C Group Network 8000 Building Automation Controls being upgraded to either BACnet or LONworks by either C&C Group or Johnson Controls? | ( | ( | ( | ( | ________________________ |
| 24. | Has the University received As-Builts for the temperature control work? | ( | ( | ( | ( | ________________________ |
| 25. | Are there graphics representing the building automation system in the Control Room? | ( | ( | ( | ( | ________________________ |
| 26. | Is the climate room monitored by the building automation system? | ( | ( | ( | ( | ________________________ |

DRAWING REVIEW CHECKLIST

ELEVATORS

PROJECT:

CONSULTANT:

PROJECT MANAGER:

DATE:

|  |  | Yes | No | N/A | F/U | Remarks |
| --- | --- | --- | --- | --- | --- | --- |
| 1. | Are all elevators/escalators non proprietary? | ( | ( | ( | ( | ________________________ |
| 2. | Have WUSM elevator standards been reviewed for specific qualifications? | ( | ( | ( | ( | ________________________ |
| 3. | For any elevator equipment room, shaft that is not directly related to the elevator, are there any penetrations of piping or conduit? | ( | ( | ( | ( | ________________________ |
| 4. | Have all elevators had a sump for a sump pump installed, including emergency receptacle for pump and control/alarm conduit to nearest BMS panel? | ( | ( | ( | ( | ________________________ |
| 5. | Does elevator have a PASS security system installed for floor access? | ( | ( | ( | ( | ________________________ |
| 6. | Is the elevator machine room HVAC on emergency power if the elevator is on emergency power? | ( | ( | ( | ( | ________________________ |
| 7. | Is a Bussmann power module used for shunt trip of the elevator power before discharge of sprinkler head? | ( | ( | ( | ( | ________________________ |
| 8. | Has an Innovative Technologies surge suppressor been connected into the Bussmann power module for protection of the elevator controller? | ( | ( | ( | ( | ________________________ |
| 9. | Has a sprinkler system been installed in the elevator machine room and shaft? | ( | ( | ( | ( | ________________________ |
| 10. | Has fire alarm smoke and detectors been installed to coordinate with sprinkler head locations? | ( | ( | ( | ( | ________________________ |

DRAWING REVIEW CHECKLIST

SPECIAL INSPECTIONS & TESTING

PROJECT:

CONSULTANT:

PROJECT MANAGER:

DATE:

|  |  | Yes | No | N/A | F/U | Remarks |
| --- | --- | --- | --- | --- | --- | --- |
| 1. | Have special inspections & testing been completed for the following? | ( | ( | ( | ( | ________________________ |
|  | Steel, concrete and masonry, wood, foundations, fire proofing and seismic components | ( | ( | ( | ( | ________________________ |
|  | Design strength of materials | ( | ( | ( | ( | ________________________ |
|  | Structural aspect of exterior walls | ( | ( | ( | ( | ________________________ |
|  | Ceilings supports details | ( | ( | ( | ( | ________________________ |
|  | Interior stud wall attachments | ( | ( | ( | ( | ________________________ |
|  | Non load bearing interior CMU walls | ( | ( | ( | ( | ________________________ |
|  | Seismic anchorage of light fixtures, diffusers, ducts, piping, and equipment | ( | ( | ( | ( | ________________________ |