## 0 GENERAL INFORMATION
RISK ASSESSMENT PACKAGE
Section I - General Information
Project Name:
Project Number:
Project Summary:
Facility:
Location Within Facility:
Project Start Date:
Estimated Project Duration:
Estimated Completion Date:
Number of Phases:
ILSM Evaluation Date:
BJC Project Manager:
BJC Project Manager Phone:
BJC Project Manager Signature:
Contractor:
Contractor Project Manager:
Contractor Project Manager Phone:
Contractor Project Manager Signature:
Project Safety Manager:
Project Safety Manager Phone:
Project Safety Manager Signature:
Facility EH&S Representative:
Facility EH&S Representative Phone:
Facility EH&S Representative Signature:
Facilities Manager:
Facilities Manager Phone:
Facilities Manager Signature:
Infection Prevention Representative:
Infection Prevention Phone:
Infection Prevention Signature:
Christian Hospital Northeast
Christian Hospital Northwest
Alton Memorial Hospital
Additional Signatures (may include: Department Manager, Project Superintendent, Subcontractors, Clinical Asset Management, IS, Security, Property Manager, etc.)
Title | Name | Date
Note: Your signature will reflect approval of entire risk assessment package.
If routed via email, routing slip is attached for verification of approval in place of actual
signatures.

## 1 PRE-WORK SAFETY & HEALTH
PRE-CONSTRUCTION/WORK SAFETY AND HEALTH CHECKLIST |  |  |  |  | Pre-Work Safety and Health Checklist
Date:
Project: |  | 0 |  |  | FALSE
Project Start Date: |  | 0
Location(Facility): |  | 0
BJC Project Manager |  | 0
Contractor Project Manager: |  | 0
Instructions: For the designated BJC Project Manager (PM) to use as a tool to ensure that items are completed and/or exchanged as part of the risk assessment process.
Y, N, N/A | Item
Completed a Pre-Construction/Maintenance Risk Assessment.
Completed an ICRA.
Completed an ILSM, or determined N/A.
Completed a Construction and Demolition Environmental Checklist, or determined N/A.
Exchanged information on the control of hazardous energy sources (lockout/tagout).
Exchanged information on electrical safe work practices/Energized work documents.
Hot work activities to be performed/Hot work permits discussed.
Safety data sheets (availability location discussed).
Required personal protective equipment on the job discussed/agreed.
Required environmental-related permits obtained.
Required Red tag permits discussed.
Additional:
Additional:
Additional:
Project Manager exchanged any required information and provided appropriate documents/forms as applicable, on behalf of BJC and the specific facility.
Contractors received copies of the relevant core and site-specific policies and procedures.
Contractor and BJC site safety contact and emergency information exchanged.
Contractors agree to send copies of site safety walkthroughs to BJC Risk Management and the facility safety representatives upon request.
Completed by: |  |  |  | Date:
Type of Event |  | Code Name/Plain Language Announcement | Explanation of Code/Example
Fire |  | Code Red or Dr. Red | Include Location of fire.
Armed Violent Intruder |  | Code Silver | Include location of affected area NOTE: Plain language can be used for this event as well. If using plain language provide direction as appropriate
Bomb Threat |  | No Code or Broad Notification | Notification should be done to a smaller group and no code or overhead notification made. It is not typical to evacuate during a bomb threat.
Evacuation |  | Evacuation and Location | Evacuation - unit 9300
Hazardous Material Spill |  | Hazardous Material Spill and Location | Hazardous Material Spill - room 2N80
Mass Casualty Event |  | Mass Casualty - Internal | Used for any patient surge due to internal emergency
|  | Mass Casualty - External | Used for any patient surge due to external emergency
|  | Mass Casualty - Decon | Used for any patient surge requiring chemical decontamination
|  | Mass Casualty - Radiation | Used for any patient surge involving radiation
Patient Abduction |  | Code Pink | Used for any pediatric patient but includes age of child and gender (i.e. Code Pink, 3 Male would be used for a three year old male) include location.
Security Code |  | Code White | Used to identify a potential aggressive situation or request for a response from a trained security team. NOTE: Plain language may be used for this event as well (see below)
Security Emergency |  | Security to (identify location) | Used for security emergency
Severe Weather |  | Activate Severe Weather Plan

## 2 PRE-CONST RISK SUMMARY
PRE-CONSTRUCTION/WORK RISK ASSESSMENT SUMMARY |  |  |  | TRUE | [7 empty] | Pre-Construction/Work Risk Assessment Summary
Classification: |  |  |  |  | Construction | Renovation |  | Demolition |  |  | Maintenance | Pre-Construction/Work Risk Assessment Summary
Project Name: |  |  | 0 |  |  |  | Facility: |  |  | 0 |  | FALSE
Project Number: |  | 0 |  |  |  |  | Location: |  | 0
Evaluation Date: |  | 0 |  |  |  |  | Start Date: |  | 0
BJC Project Manager |  | 0 |  |  |  |  | Contractor: |  | 0
Project Summary |  | 0
Describe the activities and tasks involved in the project.
Category | Potential Hazards/Mitigation Strategies (Examples listed below) |  |  |  |  | Project Specific Mitigation Strategies (if items do not apply, mark N/A in box)
Air Quality/Ventilation | Dust, fumes, mists, vapors, mold, product/task issues, location of makeup air, # of air changes, filter testing /maintenance. Assess need for monitoring.
Bloodborne Pathogens | Sharps containers, red bags.
Barrier Management | Fire wall penetrations and holes (May require ILSM and/or permit).
Emergency Preparedness | Codes, contact lists, action plans identified/discussed.
Fire/Life Safety/ILSM | Hot-work, sprinkler/fire alarm shut-off (Red-tag permit), egress, signage.
General Safety and Construction Safety hazards | PPE, fall protection (4' Rule), caught between, struck-by, ladder safety, within approach boundary of electrical equipment, etc.
Infection Prevention | Insert Risk Category and specific mitigation strategies per ICRA, attach barrier drawing.
Hazardous Materials | Items from Environmental Concerns Checklist, cleaners, medical gases, oxygen, radiation, natural gas. Provide SDS for hazardous chemicals used.
Mobile Equipment and Vehicle Operation | Emissions tier 3/4, assess need for spotters, flaggers, inspections, etc.
Noise/Vibration | Power equipment, demolition, noise & vibration, assess need to monitor and plan to mitigate as requried.
Utilities and Control of Energy Sources | Electrical access hazards, building impact, stored energy, lockout/tagout.
Special Hazards | MRI/Cryogen Safety, MRI quenching, chemical/biological/ radiological hoods/areas, radar scanner for embedded items
Security | Access control, panic alarms, badges
Other
Instructions: Check categories for potential hazards and evaluate risks. Appropriate permits, procedures and forms will need to be implemented as part of the actions taken.

## 3 ENV CONCERNS CHKLIST
ENVIRONMENTAL CONCERNS CHECKLIST | [7 empty] | CONSTRUCTION AND DEMOLITION ENVIRONMENTAL CONCERNS CHECKLIST
Project Name: | 0 |  | Project Number: | 0 |  |  |  | CONSTRUCTION AND DEMOLITION ENVIRONMENTAL CONCERNS CHECKLIST
Instructions: Complete Checklist and coordinate potential environmental issues with the EH&S Manager contact. | [7 empty] | FALSE
Subject |  | Examples |  |  | Yes | No | N/A
Aboveground Storage Tanks |  | Stained soil, abandoned tank cradle, dike or berm
(Potential) Asbestos Containing Material (PACM/ACM) |  | Floor tile, ceiling tile, pipe insulation, gaskets, transite siding, roof materials, flashing, adhesives, fire doors, lab bench tops, vermiculite
Buried Demolition Debris |  | Site history, sink hole
Chemical Solvents |  | Paints, thinners, solvents, glues, sealants, roofing materials
Chlorofluorocarbons |  | Air conditioning units, water coolers
Exit Signs |  | Tritium radiation
Exterior Excavation/Demolition Dust |  | Dust hazards associated with excavation or exterior demolition work
Generators |  | Permit for temporary generators, EPA emission documentation, pre-construction notifications
Hazardous Substances in Connection with Identified Uses/Waste Generated or Discharged |  | Oil, solvents, batteries, tires, refrigerants, absorbents, chemicals, etc.
Lead |  | Lead-based paint, drinking water/fountains, Exit/Emergency Light batteries, windows glazing, walls and doors of ex-ray rooms
Mercury |  | HID lamps, fluorescent light bulbs, various mercury switches
Mold |  | Staining, water damage, high humidity areas
Natural Occurring Radiation Materials (NORM) |  | Boiler refractory, brick, stacklining
Polychlorinated Biphenyls (PCBs) |  | Utility transformers, hydraulic elevator, hydraulic lifts, fluorescent light ballasts, etc.
Radon |  | Basements, subsurface occupancy
Railroad Ties/Treated Lumber |  | Arsenic, mercury
Silica |  | Plaster, masonry, concrete, etc.
Smoke Detectors |  | Radioactive
Topographic, Geologic & Hydrologic Site Conditions |  | Run-on, Run-off, soil disturbance, soil-type
Underground Storage Tanks |  | Abandoned vent pipes, underground piping, exterior wall penetrations
Wetlands |  | Soil disturbance, site runoff
X-ray Machines |  | Developer chemicals, fixers, lead lined walls and doors
Additional Items
Not Required for Project

## 4a IC ASSESSMENT (ICRA)
Infection Control Risk Assessment (ICRA)
Name of Project: |  | 0 |  | Project #: | 0 |  | FALSE
Location of Construction: |  | 0 |  | Project Start Date: | 0
Phasing?: |  | Yes No | How Many?: | Estimated Duration / Project End Date: | 0 | 0
Patient Relocation?: |  | Yes No |  | Contractor: | 0
Relocation area: |  |  |  | IP Representative: | 0
Facility EH&S Representative: |  | 0 |  | Facility Representative: | 0
CONSTRUCTION ACTIVITY TYPES: Mark "X" in box under type
Work Type A | Inspection and non-invasive activities, involving no dust, including but is not limited to:
· Painting (but not sanding)
· Electrical trim work, , and activities which do not generate dust or require cutting of walls or access to ceiling other then for visual inspection
Work Type B | Small scale, short duration activities which create minimal dust, including but not limited to:
· Minor plumbing
· Removal of ceiling tiles for visual inspection
· Installation of telephone and computer cabling using existing "J" hooks or wire trays
· Removal of < or = to 5 floor tiles or carpet squares
· Access to chase spaces
· Cutting a small area of a wall where dust migration can be controlled such as within a closed chase space or use of a hepavac while cutting
Work Type C | Typically large scale, longer duration activity (e.g.> one work shift) that generates a moderate to high level of dust, requires demolition or removal of any fixed building components or assemblies, including but not limited to:
· Sanding walls
· Removal > 5 floor tiles or carpet squares or removal of casework
· Any work above ceilings including J Hook or wire tray installation
· Major cabling activities
· Major demolition
· Wall covering or cove base removal
· New construction
INFECTION CONTROL RISK GROUPS: Mark "X" in box next to group number. Using the following table, identify the patient risk group that will be affected. Consider impact on areas immediatley above, below and or adjacent to the area where the active work is being performed.
Patient/Location Group 1- |  |  |  | Patient/Location Group 2-
· Cardiology |  | · All inpatient areas EXCEPT adult & pediatric oncology, and bone marrow transplant |  | · Transplant units, including Bone Marrow Transplant Unit | · All laboratory areas
· Echocardiography |  |  |  | · Intensive Care Units | · Special Care Nurseries (level 2 or >)
· Endoscopy suites |  | · Emergency Department |  | · Interventional Radiology (Special Procedures) | · Dialysis Units
· Nuclear Medicine |  | · Labor and Delivery |  | · Central Sterile Processing | · Inpatient Oncology area
· Outpatient clinics, excluding cancer clinics, transplant clinincs and chemo infusion centers |  | · Well baby nurseries |  | · Operating Room (including C-section rooms) | · Pharmacy, main and all satelites
· Pulmonary function transplant clinics |  | · Pediatrics |  | · Cancer clinics, including chemo centers, transplant clinic | · Cardiac Cath Lab/Hybrid Ors
· Kitchen, cafeteria |  | · Pre and post op areas |  | · Radiation oncology/Gamma knife/Linear accelerator/Proton therapy
· Radiology/MRI, CT |  | · Pain Management Clinic
· Respiratory Therapy |  | · Therapy Services
· Wound center |  | · Ultrasound
· Admitting |  | · Main lobby areas and/or common hallways
· Offices (e.g. no patients present) |  | · Medical Office Building/Doctors' offices
Not Required for Project

## 4b ICRA CLASS RATING
Instructions: Match the Infection Control Risk Group with the Construction Activity Type to determine the Project Class and highlight the box in yellow.
Construction Activity |  |  |  |  | FALSE
Risk Level |  | Type A (no dust) | Type B (minimal dust) | Type C (moderate / major dust)
Group 1 - |  | GREEN | YELLOW | RED
Group 2 - highest group for risk |  | GREEN | RED | RED
Job Class | Check if applicable | DURING Construction Project
GREEN |  | Interventions: |  | Additional Notes
No dust |  | Close doors to patient rooms or offices near work
Noninvasive |  | Doors closed to supply areas or cover clean supplies tightly; store supplies away from where work is performed
Inspection activities |  | Linen carts covered or moved away from where work is performed
Cover office furniture, counters and equipment with plastic; protect personal belongings as appropriate
Additional requirements not already documented:
YELLOW (in addition to Green above) |  | Interventions: |  | Additional Notes
Small amount of dust in controlled environment |  | Infection Prevention Specialist consulted at least 3 business days (72 hrs) prior to start of project.
Post signage at beginning of project if project to last > 24 hours; Responsible persons: ____________________________________
Project superintendant or HSO specific Facilities worker to check in with department manager or designee (e.g. charge nurse) at the beginning of each shift : _______Charge nurse _______Department / Office manager ________Other (specify)
Use methods to minimize migration of dust, other contaminants and or aerosolization of water, such as working within a cube, misting of ceiling surface with water (with or without bleach), appropriate plastic barrier, use of hepavac while cutting, etc.
Mist carpet tiles before removal
No patients present in active work area
Materials being brought to project site should be covered/wrapped
Debris removed in covered containers
Designate an elevator or route for debris removal when necessary
Open penetrations must be covered if unattended (e.g. plastic, dry wall, etc)
Access panels without barriers must be closed if unattended
Ceiling tiles replaced ASAP and must be closed if unattended
Walk off sticky mats
Clean work site at end of workday.
HEPA machine in area as air scrubber. Designate location of machine: __________________________
Additional requirements not already documented:
RED (in addition to Green+Yellow above) |  | Interventions: |  | Additional Notes
Patients to wear masks when entering or leaving HSO. Notification responsibility person: ____IP ______Other (Specify)
Barriers constructed and inspected by IP prior to beginning work
Barrier type: ____Air tight soft (plastic) wall (acceptable if work lasts 72-96 hrs or less per discretion of IP/Safety); ____ Airtight hard wall partition (floor to deck); _______Airtight hard wall partition (floor to ceiling)
Ceiling plastic curtain required
Barrier seams taped
Maintain negative air flow within constuction site (Note: cap off air supply if necessary to achieve negative pressure)
Check pre filters on fans or units used to maintain negative airflow (commonly HEPA) at least daily or more frequently if major demolition
Use visual monitor/aide for negative air pressure.
Contractor to document at least daily that negative pressure is being maintained.
Return air vents blocked or sealed before beginning work if applicable.
Monitor and change return vent filters as needed and document.
Workers to remove dust from clothing prior to entering any hospital areas; e.g. sticky mats, vacuum clothing, apply clean clothing or remove coveralls and shoe coverings
When going thru sensitive areas, protective attire (PA) must be worn to access anteroom and work area. PA must be removed before entering the work area because it will be used again to exit through the sensitive area.
Keep work area clean e.g. wet mop or HEPA vac frequently ______X per day to decrease risk of tracking dust through clean areas
Wet mat (may consider 10% bleach solution); If using both sticky mas and wet mats, order should be wet mat, dry mat, sticky mat)
Create an ante room (ORs, hemonc/BMT units, large areas where negative pressure difficult to achieve, etc)
Mist outdoor construction site frequently and as needed to prevent dust aerosolization
Wet cut cement
Assess location of air intakes for outdoor projects and/or projects where work is being done < 75 ft from intakes- additional or higher filtration may be requried to avoid entry of contamination (e.g. dust and debris) of air intakes
Partner with EH&S to determine if air sampling (e.g. particle counts) is required during the project.
Additional requirements not already documented:
Not Required for Project

## 5a ILSM
Life Safety Compromise/Impairment |  |  | CONSTRUCTION ILSM/ALSM ASSESSMENT TOOL | [18 empty] | CONSTRUCTION ILSM/ALSM ASSESSMENT TOOL
CONSTRUCTION ILSM/ALSM ASSESSMENT TOOL
|  |  | Yes* | No | a) ensure egress | b) emergency forces access | c) notify Security | d) ensure operational life safety systems | e) temporary construction barriers | f) additional fire fighting equipment and associated training | g) prohibit smoking | h) control combustible loading | i) hold 2 fire drills/shift in affected areas | j) increased hazard surveillance | k) provide staff structural or compartmentation training | l) education for affected staff | m) notification FD if out of svc >4 hrs. in 24 hr. period | Notify FM Global (red tag) | Notify Facility Management (*immediately) | Post signage | Notify Safety (*Immediately) | FALSE
FALSE
Location(s) Affected: |  | 0
Start Date: |  | 0
Completion Date: |  | 0
ILSM/ALSM Evaluation Date: |  | 0
Staff Member Assigned
construction maintenance SOC
Life Safety Systems
DEFICIENCIES | Failure or disabling of any existing fire alarm system initiating device (pull station, smoke detector) | [5 empty] | X | X | See Temporary Construction Barriers Policy SA38P1 |  | X |  |  | X |  | X |  |  | X | >8 hr. | X
| Failure or disabling of any fire alarm system notification device – audible/speakers and visual devices | [5 empty] | X | X |  |  | X |  |  | X |  | X |  |  | X | >8 hr. | X
| Failure or disabling of the proprietary station notification system | [5 empty] | X | X |  |  | X | [5 empty] | >4 hr./24 |  | X* |  | X*
| Fire pump planned shutdown or failure | [5 empty] | X | X |  | X | X | X |  | X |  |  | >10 hr./24 | X | X* |  | X*
| Main drain test failure | [6 empty] | X |  |  | X | X |  |  |  |  | >10 hr./24 | X | X |  | X
| Failure or disabling of standpipe and/or sprinkler connections for the fire department | [5 empty] | X | X |  | X | X | X |  | X |  |  | >10 hr/24 | X | X* |  | X*
| Failure or disabling of area specific fire suppression system (kitchen hoods, FM200 systems) | [6 empty] | X |  | X | X | X |  |  |  | X | >10 hr/24 | X | X* |  | X*
| Failure or disabling of a fire/smoke damper | [6 empty] | X |  |  | X | X | > 1mo |  | X |  |  |  | X |  | X
| Failure or disabling of fire alarm system shut down devices for AHUs | [6 empty] | X |  |  | X | [7 empty] | X |  | X
| Replacing fire alarm system | [5 empty] | X | X |  |  | X |  |  | X |  |  | >4 hr./24 |  | X* |  | X*
| Installing/renovating sprinkler system | [5 empty] | X | X |  | X | X |  |  | X |  | X | >10 hr/24 | X | X |  | X
| Significantly modifying smoke/fire barriers |  |  |  | X |  | X | X |  |  | X | X | > 1mo | X | X |  |  |  | X | X | X
| Failure or disabling of any function of the fire alarm system main building panel or sub-panel | [5 empty] | X | X |  |  | X | X |  | X |  | X | >4 hr/24 |  | X* |  | X*
| Multiple ceiling tiles removed with sprinkler heads/smoke detectors left in the same plane | [5 empty] | X | X |  | X | X | X |  | X |  |  |  |  | X* |  | X*
| Failure or disabling of a sprinkler system | [5 empty] | X | X |  | X | X | X |  | X |  | X | >10 hr/24 | X | X* |  | X*
Life Safety Compromise/Impairment |  |  | INTERIM LIFE SAFETY MEASURES
|  |  | Yes* | No | a) ensure egress | b) emergency forces access | c) notify Security | d) ensure operational life safety systems | e) temporary construction barriers | f) additional fire fighting equipment and assoc. training | g) prohibit smoking | h) control combustible loading | i) hold 2 fire drills/shift in affected areas | j) increased hazard surveillance | k) provide staff structural or compartmentation training | l) education for affected staff | m) notification FD if out of svc >4 hrs. in 24 hr. period | Notify FM Global (red tag) | Notify Facility Management (*immediately) | Post signage | Notify Safety (*Immediately)
Location(s) Affected |  | 0
Start Date |  | 0
Completion Date |  | 0
ILSM/ALSM Evaluation Date |  | 0
Staff Member Assigned
Access & Egress
DEFICIENCIES | Failure or disabling of roll down (shutter) or sliding fire doors or other fire separation features | [6 empty] | X | See Temporary Construction Barriers Policy SA38P1 |  | X |  | > 1mo |  | X | X |  |  | X | >8 hr. | X
| Patient room door latching failure | [9 empty] | X | [7 empty] | X
| Non functioning exit signs |  |  |  | X | [5 empty] | X | [7 empty] | X
| Broken fire/smoke doors |  |  |  | X |  |  | X |  |  | X | X | > 1mo |  | X |  |  |  | X | >8 hr. | X
| Unlabeled (rated) fire/smoke door | [9 empty] | X | [7 empty] | X
| Blocking off an approved exit |  |  |  | X | X |  | X |  |  | X | X | > 1mo |  | X |  |  |  | X* | X | X*
| Rerouting of traffic to emergency room |  |  |  | X | X | X |  |  |  | X |  |  | X |  | X | >4 hr./24 |  | X* | >8 hr. | X*
Construction Related
| Improperly protected vertical openings | [6 empty] | X |  |  | X | X | > 1mo |  | X |  |  |  | X |  | X
| Penetrations in fire/smoke barriers | [5 empty] | X | X |  |  | X | X | > 1mo | X | X |  |  |  | X |  | X
| Corridor walls do not extend to structure | [5 empty] | X | X |  |  | X | X | > 1mo | X | X |  |  |  | X |  | X
| Build out of temporary structure (ex. temp partition) into exit corridor |  |  |  | X |  |  | X |  |  | X | X | > 1mo | [5 empty] | X* | >8 hr. | X*
Hazardous Materials
| Hazardous area not properly protected. (Mechanical/shop area, linen rms., trash rms., labs, kitchen, etc.) | [5 empty] | X | X |  | X | X | X | > 1mo | X | X | X |  |  | X* |  | X*
| Open flame/Hot work activity (*contact Safety for permit and initiate Hot Work Policy) |  | #3 |  |  |  | X | X |  |  | X | X |  | X |  |  |  |  | X
Evaluation Results: |  | 1) ILSM/ALSM are not required because: |  |  | No life safety features will be compromised.
|  | 2) ILSM/ALSM are required |  |  |  |  | If "yes", daily ILSM/ALSM Checklist must be initiated
3) Initiate Hot Work Policy
Please Note: |  | Any "Yes" requires ILSM/ALSM to be implemented (with exception of hot work, which initiates the Hot Work policy implementation.) Detailed
information on specific processes should be included in the Pre-Construction Risk Assessment form.
Facility Staff Signature: | [6 empty] | Date:
Facility Operations Signature: | [6 empty] | Date:
Manager, EH&S Signature: | [6 empty] | Date:
Project Manager Signature: | [6 empty] | Date:
Contractor Signature: | [6 empty] | Date:
Security, if applicable:
* Signatures are not required on this page if this ILSM/ALSM is completed as part of a project risk assessment package.
Not Required for Project

## 5b ILSM CHECKLIST
INTERIM/ALTERNATE LIFE SAFETY MEASURES CHECKLIST | [17 empty] | INTERIM/ALTERNATE LIFE SAFETY MEASURES CHECKLIST
Project Name: |  | 0 | [15 empty] | INTERIM/ALTERNATE LIFE SAFETY MEASURES CHECKLIST
Project Number: |  | 0 | [15 empty] | FALSE
ITEM |  |  | DAILY INSPECTIONS
|  |  | Date: |  |  | Date: |  |  | Date: |  |  | Date: |  |  | Date:
|  |  | Yes | No | N/A | Yes | No | N/A | Yes | No | N/A | Yes | No | N/A | Yes | No | N/A
1 | All exits are unobstructed & useable, including construction area and adjacent areas.
2 | Alternate routes are identified if required.
3 | All personnel have training if alternate exits have been designated.
4 | Construction workers know the means of egress.
5 | There is free & unobstructed means to access emergency services.
6 | The fire alarm detection and suppression systems are not impaired.
7 | A temporary, but equivalent system is provided when fire system is impaired.
8 | Before the fire alarm systems are taken out of service, steps are taken to compensate, including notification of appropriate authority having jurisdiction. (i.e. local fire department, insurance carrier, etc.)
9 | Temporary construction partitions are smoke tight and built of noncombustible or limited combustible material.
10 | Construction area is properly restricted from the rest of the facility with appropriate signage. Access to construction area is limited to authorized personnel.
11 | Smoking is prohibited in the construction area, and adjacent areas.
12 | Construction area is clean and orderly. Storage, housekeeping, and debris removal practices are enforced to reduce the flammability and combustibility fire load of the building to the minimum necessary to conduct daily operation.
13 | Additional firefighting equipment and its associated training has been provided to personnel.
14 | Fire watch program is established, and personnel are instructed as to the nature of the job, and the nature of the work in progress.
For items checked "No" include a description of the deficiency and corrective action steps on the back of this form or in an equivalent manner.
Contractor Representative or Project Manager: |  |  | Date:
Not Required for Project

## 6b ELEC SAFE WORK CONDITIONS
ESTABLISHING ELECTRICAL SAFE WORK | [5 empty] | ESTABLISHING ELECTRICAL SAFE WORK
Project Name: |  | 0 |  |  |  | ESTABLISHING ELECTRICAL SAFE WORK
An electrical safe work condition does not exist until all of the six steps have been completed. Until then, employees could contact an exposed live part, and they must wear appropriate PPE. Use this checklist to document establishing an electrical safe work condition. Completed document should be filed with completed shutdown request. | [5 empty] | FALSE
1. Determine all possible sources of electrical supply to the specific equipment. Verify up-to-date drawings, diagrams, maintenance records and identification tags.
| Above are complete and updated? | Yes | No | If no, explain.
Number of sources identified:
| Name of person completing: |  |  |  | Date:
2. After properly interrupting the load current, open the disconnecting device(s) for all sources.
| Completed? | Yes | No | If no, explain.
| Name of person completing: |  |  |  | Date:
3. Wherever possible, visually verify that all blades of the disconnecting devices are fully open or that drawout-type circuit breakers are withdrawn to the fully disconnected position.
| Completed? | Yes | No | If no, explain.
| Name of person completing: |  |  |  | Date:
4. Apply lockout/tagout devices in accordance with a documented and established policy.
| Completed? | Yes | No | If no, explain.
| Name of person completing: |  |  |  | Date:
5. Use an adequately rated voltage detector to test each phase conductor or circuit part to verify they are de-energized. Test each phase conductor or circuit part both phase-to-phase and phase-to-ground. Before and after each test, determine that the voltage detector is operating satisfactorily.
| Voltage detected? | Yes | No | If yes, explain.
| Name of person completing: |  |  |  | Date:
6. Where the possibility of induced voltages or stored electrical energy exists, ground the phase conductors or circuit parts before touching them. Where it could be reasonably anticipated that the conductors or circuit parts being de-energized could contact other exposed energized conductors or circuit parts, apply ground connecting devices rated for the available fault duty.
| Grounding devices applied? | Yes | No | N/A
| Name of person completing: |  |  |  | Date:
Not Required for Project

## 6c ENERGIZED ELECT PERMIT (ON)
ENERGIZED ELECTRICAL WORK PERMIT - ON
Hazard Identification and Risk Assessment Procedures
INSTRUCTIONS: No work may be performed until permit is completed AND signed by both parties. Permit must be complete when planning work on energized electrical conductors or circuit parts. Permit becomes void: 1) at end of shift or expiration time, whichever occurs first, or 2) when conditions change significantly, or 3) on an emergency signal. | [9 empty] | FALSE
Requestor Name and Company: | [6 empty] | Date Requested
Work Order/Project #: |  | 0 |  |  |  |  | Start Date: |  |  |  |  | Time:
Shutdown Request#: | [6 empty] | End Date: |  |  |  |  | Time:
Building: |  | 0 |  |  |  |  | Department:
Location of Required Work (be specific): |  |  | 0
Description of Work ( for work on battery systems identify chemical hazard also):
What is the maximum possible injury that could result? |  |  |  |  | Shock |  | Electrocution |  |  |  | Arc Flash
Will the worker be within the shock and/or arc flash boundary of the equipment that presents the possible exposure? Yes No
Contact Name of Worker: |  |  |  | Title: | [5 empty] | Telephone:
Facility Contact Name |  |  |  | Title: | [5 empty] | Date into received
Required Work Procedure/Method of Procedure (MOP) provided? | [6 empty] | Yes |  | No
Note: An MOP is a detailed description of work to be performed as outlined by the Contractor/Project Manager
Identification of Equipment - Electrical Hazard Analysis Information (from Arc Flash sticker/table & nameplate)
Information obtained from: Arc Flash Sticker | [5 empty] | NFPA 70E Hazard/Risk Category Table (if no study available)
Manufacturer |  |  |  |  | Model
System Voltage |  |  |  |  | Shock Hazard
Amperage |  |  |  |  | Limited Approach Boundary
Hazard Risk Category |  |  |  |  | Restricted Approach Boundary
Arc Flash Boundary |  |  |  |  | Prohibited Approach Boundary
Facility, Equipment, and Installation Information
Information/drawings on facility equipment, installation and circuitry available/current? | [9 empty] | Yes |  | No | If No, explain
Qualified person available to provide assistance and be a resource? | [9 empty] | Yes |  | No | If No, explain
Vendor information on equipment to be worked on available? | [9 empty] | Yes |  | No | If No, explain
One-line drawings current/available on site for reference? | [9 empty] | Yes |  | No | If No, explain
Current status and condition of equipment to be worked on verified? | [9 empty] | Yes |  | No | If No, explain
Personal Protective Equipment and Tools Required
| Arc Rated Flash Suit Hood |  |  |  | Arc Rated Flash Suite Jacket |  |  |  |  | Safety Glasses/Goggles
| Arc Rated Long Sleeve Shirt |  |  |  | Arc Rated Flash Suite Pants |  |  |  |  | Hearing Protection
| Arc Rated Pants |  |  |  | Heavy Duty Leather Work Gloves |  |  |  |  | Insulation Materials
| Arc Rated Coveralls |  |  |  | Hard Hat |  |  |  |  | Barrier Tape/Cones
| Arc Rated Face Shield w/ Balaclava |  |  |  | Arc Rated Work Gloves w/Leather Protectors |  |  |  |  | Insulation Blankets
[5 empty] | Leather Work Boots/Shoes |  |  |  |  | V-Rated Tools
Emergency Preparedness
Emergency Contact: | [6 empty] | Telephone Number:
Location of Nearest Fire Extinguisher: | [6 empty] | Mobile/Radio Communication:
Location of Fire Alarm Signals: | [6 empty] | First Aid Kit/AED Location:
Areas served and contingency plan:
REQUIRED AUTHORIZATION
Energized work on this circuit/equipment is: |  |  |  |  | Not Authorized |  |  | Authorized
Signature (Facility Operations Manager, or designee)* | [9 empty] | Date:
Signature (BJC/Entity EH & S, or designee)* | [9 empty] | Date:
Signature (BJC/Entity Project Manager, or designee) | [9 empty] | Date:
Signature (Contractor/Staff) | [9 empty] | Date:
*Typed name may serve as actual signature; permit requires all signatures; *must be present for EH & Safety review
Not Required for Project

## 7 SYSTEMS SHUT-DOWN REQUEST
SYSTEMS SHUT-DOWN/RESEARCH REQUEST
Must have ( ) business days ' notice
RESEARCH REQUEST |  |  |  |  | SHUTDOWN REQUEST
TO BE COMPLETED BY CONTRACTOR/ENGINEER
SYSTEMS AFFECTED |  |  |  |  | TODAY'S DATE
DOMESTIC HOT WATER |  | VENTILATION |  |  |  | SPRINKLER SYSTEM
DOMESTIC COLD WATER |  |  | SUPPLY AIR |  |  | LIGHT CIRCUIT
WASTE/VENT |  |  | EXHAUST AIR |  |  | POWR CIRCUIT
MEDICAL GAS |  |  | RETURN AIR |  |  |  | EMERGENCY POWER
| VACUUM | TEMPERATURE CONTROL |  |  |  |  | UPS
| AIR | STEAM HEAT PIPING |  |  |  |  | STANDARD POWER
| OXYGEN | SECURITY SYSTEM |  |  |  | EMERGENCY SYSTEMS
| OTHER | CHILLED WATER |  |  |  | SMOKE DETECTORS
OTHER | [5 empty] | FIRE ALARM SYSTEM
DATE OF PROPOSED SHUTDOWN |  |  |  | TIME OF DAY
DURATION
LOCATION OF WORK
PROJECT MANAGER NAME/PHONE/EMAIL
GENERAL CONTRACTOR NAME/COMPANY/PHONE
SUB COMPLETING WORK
SUB CONTACT NAME/PHONE
PERSON PERFORMING RESEARCH
CONTRACTOR SIGNATURE
TO BE COMPLETED BY FACIILITY MANAGER
NAME |  |  |  |  | TODAY'S DATE
THE FOLLOWING MUST BE NOTIFIED (CHECK WHEN COMPLETE) |  |  |  |  | OTHER OCCUPANTS IMPACTED:
ENGINEERING
SECURITY
SAFETY
INFECTION PREVENTION
*CONTRCTOR MUST AGAIN NOTIFY THOSE CHECKED 2 HOURS BEFORE SHUTDOWN
FACILITY RESPONSE TO CONTRACTOR/ENGINEER
APPROVED AS PROPOSED
APPROVED BASED ON THE FOLLOWING
DENIED-EXPLAIN WHY
| FACILITY REQUESTS ALTERNATE SHUTDOWN TIME: |  |  |  | ADDITIONAL INFORMATION IS NEEDED PRIOR TO START OF ANY WORK
NOTE ANY FACILITY SPECIFIC INFO CONTRACTOR MUST BE AWARE OF PRIOR TO WORK
(Unique electrical configuration, chemical hazards in area, etc.):
| Facilities Approval: |  |  |  |  | Date:
| Contractor Approval: |  |  |  |  | Date:
LOG NUMBER ASSIGNED
SPECIFIC AREAS IMPACTED BY SHUTDOWN
Attach a DETAILED work plan/drawing indicating specific system information